Product Specification Guide
Model Motor Starter Standard Control (MSSC)

************************************************************************************************************************
Note to User: This document is subject to copyright protection and is proprietary to Greenheck Fan Corporation.  However, Greenheck Fan Corporation authorizes the user a limited non-exclusive license to use this document or portions of it for the purpose of preparing written product specifications for the above CSI MasterFormat category.  All information in this document as provided by Greenheck Fan Corporation is informational in nature and is provided without representation or warranty of any kind as to the user or any other party, including, without limitation, ANY IMPLIED WARRANTY OF MERCHANTABILITY, FITNESS FOR PARTICULAR PURPOSE, OR NON-INFRINGEMENT.  To the greatest extent permitted by applicable law, Greenheck Fan Corporation assumes no liability, and User assumes all liability and risk, for the use or results from the use of this document or the information contained herein, whether as modified by the user or not.  Users should consult www.greenheck.com to verify that this document represents the most current version.
************************************************************************************************************************

Magnetic Motor Starters for 3 phase motors shall be enclosed in a 16 gauge steel, industrial polyurethane coated enclosure with the appropriate environmental rating. Starters shall consist of a horsepower rated magnetic contactor, a minimum of one Normally Open and one Normally Closed auxiliary control contacts and solid state electronic overload relay. Overload relay shall protect all three phases with an adjustable current setting of 1-40 amps to allow ﬁeld adjustment for speciﬁc motor Full Load Amps (FLA). Interchangeable heater elements are not acceptable.

The overload relay must provide the following motor protection features: if the FLA on the overload is set outside an acceptable range to properly protect the motor, the overload must trip and close a contact to indicate fault event. Overload relay shall provide phase failure, phase loss, cycle fault and stall protection. Overload must detect a locked rotor upon startup and trip within 0.5 seconds if such condition is detected. Overload must also monitor motor inrush current on startup and if detected FLA does not reach nominal running amps within 10 seconds, trip and stop the motor. Provide ﬁeld selectable manual or automatic reset of overload as well as reset pushbutton on the starter cover to restore normal operation after a trip or fault condition. In the event of a power failure, starter shall restart in last known operating mode.

When the starter is remotely controlled by an automation system, the starter shall include remote run terminals which accept both a voltage input signal and a contact closure. The voltage run input shall accept both AC and DC signals from 12-250V to allow direct connection of the transistorized automation signal to the starter. Starter must contain an integral current sensor with Normally Open contact which closes to indicate motor run status.

Installed accessories shall include Hand-Off-Auto operation switch with LED pilot light indicators for Hand, Off, Auto, Run and Overload conditions. All pilot devices shall be water tight and dust tight. Manufacturer shall provide and install tags with engraved lettering to designate equipment served. All starters must be provided with a universal power supply capable of a 200 to 600 volt input range.

Enclosed combination starters shall include all of the magnetic starter requirements in addition to a disconnecting method in accordance with National Electrical Code. Each disconnect shall be of the Motor Circuit Protector type, carry a UL 508F rating and provide a minimum interrupting rating of 30,000 Available Interrupting Current (AIC) for the combination starter. All disconnects shall include a lock-out mechanism when in the off position.