Product Specification Guide
Direct Drive, Backward curved Plenum Fan, Model APD
Facility Services Subgroup: Division 23 (Previously Division 15)

*****************************************************************************************************************
Specifier Notes: This product specification guide is written in accordance to the Construction Specifications Institute (CSI) Format - 2004 Edition.

This section must be carefully reviewed and edited by the Engineer to meet the requirements of the project and local building code. Coordinate with other specification sections and the drawings.

Delete all unnecessary “Specifier Notes” when editing this section.

Note to User: This document is subject to copyright protection and is proprietary to Greenheck Fan Corporation. However, Greenheck Fan Corporation authorizes the user a limited non-exclusive license to use this document or portions of it for the purpose of preparing written product specifications for the above CSI MasterFormat category. All information in this document as provided by Greenheck Fan Corporation is informational in nature and is provided without representation or warranty of any kind as to the user or any other party, including, without limitation, ANY IMPLIED WARRANTY OF MERCHANTABILITY, FITNESS FOR PARTICULAR PURPOSE, OR NON-INFRINGEMENT. To the greatest extent permitted by applicable law, Greenheck Fan Corporation assumes no liability, and User assumes all liability and risk, for the use or results from the use of this document or the information contained herein, whether as modified by the user or not. Users should consult www.greenheck.com to verify that this document represents the most current version.
*****************************************************************************************************************

1.	GENERAL
1.1	WORK INCLUDED  
A.	Direct Drive Backward Curved Plenum Fan, Model APD

1.2	RELATED SECTIONS 
A.	All sections, drawing plans, specifications and contract documents.

1.3	REFERENCES
A.	ANSI/AMCA Standard 99-10, “Standards Handbook” 
B.	ANSI/AMCA Standard 204-05, “Balance Quality and Vibration Levels for Fans”
C.	ANSI/AMCA Standard 210-07, “Laboratory Methods of Testing Fans for Aerodynamic Performance Rating”
D.	AMCA Publication 211-05, “Certified Ratings Program – Product Rating Manual for Fan Air Performance”
E.	ANSI/AMCA Standard 300-08, “Reverberant Room Method for Sound Testing of Fans”
F.	AMCA Publication 311-05, “Certified Ratings Program – Product Rating Manual for Fan Sound Performance”
G.	AMBA - Method of Evaluating Load Ratings of Bearings ANSI-11 (r1999).
H.	OSHA guideline 1910.212 – General requirements for Machine Guarding. (www.osha.gov)
I.	OSHA guideline 1910.219 – General requirements for guarding safe use of mechanical power transmission apparatus.  (www.osha.gov)
J.	OSHA guideline 1926.300 – General requirements for safe operation and maintenance of hand and power tools. (www.osha.gov)

*****************************************************************************************************************

1.4	QUALITY ASSURANCE
A.	Performance ratings: Conform to ANSI/AMCA Standards 210 and 300. Fans must be tested in accordance with AMCA Publications 211 and 311 in an AMCA accredited laboratory and certified for air and sound performance. Fans shall be licensed to bear the AMCA ratings seal for air performance (AMCA 210) and sound performance (AMCA 300).
B.	Fans shall have a Fan Energy Index (FEI) rating that meets or exceeds requirements of the latest edition of ASHRAE 90.1.
C.	Fans shall be licensed to bear the Air Movement and Control Association (AMCA) Certified Ratings Program (CRP) seal for FEI.
D.	The Fan FEI rating shall be indicated on the design documents and manufacturer product submittals to allow for compliance verification by the building official.
E.	Comply with the National Electrical Manufacturers Association (NEMA) standards for motor and electrical accessories.

1.5	SUBMITTALS
A.	Provide dimensional drawings and product data on each fan.
B. 	Provide fan curves for each fan at the specified operation point, with the flow, static pressure and horsepower clearly plotted.
C.	Provide both inlet sound power reading. 
D.	Strictly adhere to QUALITY ASSURANCE requirements as stated in section 1.4 of this specification.

1.6	DELIVERY, STORAGE AND HANDLING
A.	Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly indicating manufacturer, material, products included and location of installation.
B.	Store materials in a dry area indoor, protected from damage and in accordance with manufacturer’s instructions. For long term storage, follow manufacturer’s Installation, Operation and Maintenance manual.
C.	Handle and lift fans in accordance with the manufacturer’s instructions. Protect materials and finishes during handling and installation to prevent damage. Follow all safety warnings posted by the manufacturer.

1.7	WARRANTY
A.	Submit, for Owner's acceptance, manufacturer's standard warranty document executed by authorized company official. Manufacturer's warranty is in addition to, and not a limitation of, other rights Owner may have under Contract Documents.
1.	The warranty of this equipment is to be free from defects in material and workmanship for a period of one year from the purchase date. Any units or parts which prove defective during the warranty period will be replaced at the manufacturers’ option when returned to the manufacturer, transportation prepaid.
2.	Motor Warranty is warranted by the motor manufacturer for a period of one year. Should motors furnished prove defective during this period, they should be returned to the nearest authorized motor service station.

2.	PRODUCTS
2.1	GENERAL
A.  	Base fan performance at standard conditions (density 0.075 lb. /ft3).
B.	Fans selected shall be capable of accommodating static pressure and flow variations of +/-15% of scheduled values.
C.	Each fan shall be direct drive in AMCA arrangement 4 only according to drawings. 
D.	Fans are to be equipped with lifting points.

2.2	FAN HOUSING
A.	Plenum fans shall be of the unhoused direct drive backward curved type.
B.	Fan plate shall be aerodynamically designed with high-efficiency inlet, engineered to reduce incoming air turbulence.
C.	Panels and framework shall be constructed of precision laser cut and die formed galvanized steel to provide a rigid structure to support the motor and reduce low frequency vibration.
D.	Fan base angles shall be recessed to reduce overall width of the assembly.
E.	Each fan shall be given an electronic vibration analysis in accordance with ANSI/AMCA Standard 204, while operating at the specified fan RPM. The vibration signatures shall be taken at motor mounting pedestal in the horizontal, vertical and axial direction. The maximum allowable fan vibration shall be 0.10 in. /sec peak velocity, filter-in as measured at the fan RPM. 

2.3	FAN WHEEL
A.	The fan wheel shall be backward curved type. Wheels shall be statically and dynamically balanced to balance grade G6.3 per ANSI S2.19.
B.	The fan wheel shall be manufactured with a minimum of seven, stich welded blades and finished with a protective coating to inhibit corrosion.  
C.	The wheel and fan inlet shall be carefully matched and shall have precise running tolerances for maximum performance and operating efficiency. 

2.4	FAN MOTOR
A.	Motors shall meet or exceed EISA (Energy Independence and Security Act) efficiencies.  Motors shall be NEMA T-frame, 1200, 1800 or 3600 RPM in 60 Hz (1000, 1500 or 3000 RPM in 50 Hz), Open Drip Proof (ODP) [Totally Enclosed Fan Cooled (TEFC), with a 1.15 service factor. 
B.	Motors shall be variable frequency drive (VFD) compatible with internal shaft grounding ring to ground induced voltages created from the use of a VFD.

3.	EXECUTION
3.1	EXAMINATION
A.	Examine areas to receive fans. Notify the Engineer of conditions that would adversely affect installation or subsequent utilization and maintenance of fans. Do not proceed with installation until unsatisfactory conditions are corrected.

3.2	INSTALLATION
A.  	Install fans systems as indicated on the contract drawings.
B. 	Install fans in accordance with manufacturer’s Installation, Operation and Maintenance manual.

4.	ACCEPTABLE MANUFACTURERS
A.	Greenheck Fan Corporation, PO Box 410, Schofield WI 54476-0410, www.greenheck.com, Model APD, Direct Drive Backward Curved Plenum Fan.